## Sheet1
30 | 100 | 4x10/4G | THW | 1-1/4" IMC
40 | 100 | 4x16/4G | THW | 1-1/2" IMC
50 | 100 | 4x25/6G | THW | 2" IMC
60 | 100 | 4x25/6G | THW | 2" IMC
70 | 100 | 4x35/6G | THW | 2" IMC
80 | 100 | 4x50/6G | THW | 2-1/2" IMC
90 | 100 | 4x50/6G | THW | 2-1/2" IMC
100 | 100 | 4x70/10G | THW | 2-1/2" IMC
125 | 250 | 4x95/16G | THW | 3" IMC
150 | 250 | 4x95/16G | THW | 3" IMC
175 | 250 | 4x120/16G | THW | 3" IMC
200 | 250 | 4x150/16G | THW | 3" IMC
225 | 250 | 4x185/16G | THW | 3-1/2" IMC
250 | 250 | 4x240/16G | THW | 4" IMC
300 | 400 | 8x95/16G | THW | 2x3" IMC
350 | 400 | 8x120/16G | THW | 2x3" IMC
400 | 400 | 8x150/25G | THW | 2x3" IMC
450 | 600 | 8x185/25G | THW | 2x3-1/2" IMC | 8x1C-120/2x35G | NYY | 2x3" HDPE
500 | 600 | 8x240/25G | THW | 2x4" IMC
600 | 600 | 8x300/25G | THW | 2x4" IMC
700 | 1000 | 12x185/35G | THW | 3x4" IMC
800 | 1000 | 12x240/50G | THW | 3x4" IMC

## MDB
PANEL BOARD LOAD SCHEDULE
PANEL NO. : |  | MDB |  |  |  | LOCATION : | FLOOR 1
CONNECTED TO : |  | TRANSFORMER 100 KVA |  |  |  | CAPACITY :
CCT | DESCRIPTION | LOAD (VA) |  |  | CB |  |  | CABLE | TYPE. | COND.
N0. |  | PHASE A | PHASE B | PHASE C | P | AT | AF
1 | LC1 | 5940 | 5520 | 3840 | 3 | 50 | 100 | 3x16/10/6G | THW | 1-1/4" | 3750 | 27
2 | DB2 | 4416 | 2784 | 4416 | 3 | 50 | 100 | 3x25/16/6G | THW | 1-1/2" | 7500
3 | DB3 | 4416 | 2784 | 4416 | 3 | 50 | 100 | 3x25/16/6G | THW | 1-1/2" | 15000
4 | DB4 | 4416 | 2784 | 4416 | 3 | 50 | 100 | 3x25/16/6G | THW | 1-1/2" | 30000
5 | DPR | 10800 | 10800 | 10800 | 3 | 60 | 100 | 3x25/16/6G | THW | 1-1/2" | 60000
6 | CP-PUMP | 3500 | 3500 | 3500 | 3 | 30 | 100 | 4x25/10G | THW
| VA / PHASE | 33488 | 28172 | 31388 | MAIN CB. |  |  | MAIN CABLE
| TOTAL |  | 93048 | VA. | P | AT | AF | CABLE | TYPE. | COND.
| DEMAND LOAD /PHASE | 28464.8 | 23946.2 | 26679.8 | 3 | 150 | 250 | 3x95/1x70 | THW | 3"
| TOTAL LOAD |  | 79090.8 | VA. | BRANCH CIRCUIT BREAKER IC 25 KA AT 240 V
| AMP. / PHASE | 129.3855 | 108.8464 | 121.2718
98863.5

## LC1
PANEL BOARD LOAD SCHEDULE
PANEL NO. : |  | LC1 |  |  |  | LOCATION : | FLOOR 1
CONNECTED TO : |  | MDB |  |  |  | CAPACITY : | 18 | cct
CCT | DESCRIPTION | LOAD (VA) |  |  | CB |  | CABLE | TYPE. | COND.
N0. |  | PHASE A | PHASE B | PHASE C | P | AT
1 | LIGHTING | 1900 |  |  | 1 | 15 | 2x2.5 | THW | 1/2" | 3750 | 8.6364
3 | LIGHTING |  | 2000 |  | 1 | 15 | 2x2.5 | THW | 1/2" | 7500
5 | LIGHTING |  |  | 1200 | 1 | 15 | 2x2.5 | THW | 1/2"
7 | LIGHTING + RECEPTACLE | 1600 |  |  | 1 | 15 | 2x2.5/1.5G | THW | 1/2"
9 | LIGHTING ทางเดิน |  | 1600 |  | 1 | 15 | 2x2.5 | THW | 1/2"
11 | LIGHTING + RECEPTACLE |  |  | 1100 | 1 | 15 | 2x2.5/1.5G | THW | 1/2"
13 | SPARE | 2500 |  |  | 1 | 15
15 | SPARE |  | 2500 |  | 1 | 15
17 | SPARE |  |  | 2500 | 1 | 15
2 | LC11 | 2400 |  |  | 1 | 30 | 2x10/4G | THW | 1"
4 | RECEPTACLE |  | 1600 |  | 1 | 15 | 2x2.5/1.5G | THW | 1/2"
6 | RECEPTACLE |  |  | 1600 | 1 | 15 | 2x2.5/1.5G | THW | 1/2"
8 | AIR CONDITION | 1500 |  |  | 1 | 20 | 2x4/1.5G | THW | 1/2"
10 | AIR CONDITION |  | 1500 |  | 1 | 20 | 2x4/1.5G | THW | 1/2"
12
14
16
18
| VA / PHASE | 9900 | 9200 | 6400 | MAIN CB. |  | MAIN CABLE
| TOTAL |  | 25500 | VA. | AT | AF | CABLE | TYPE. | COND.
| DEMAND LOAD /PHASE | 5940 | 5520 | 3840 | 50 | 100 | 3x16/10/6G | THW | 1-1/4"
| TOTAL LOAD |  | 15300 | VA. | BRANCH CIRCUIT BREAKER IC 18 KA AT 240 V
| AMP. / PHASE | 27 | 25.0909 | 17.4545

## LC11
PANEL BOARD LOAD SCHEDULE
PANEL NO. : |  | LC11 |  | LOCATION : | FLOOR 1
CONNECTED TO : |  | LC1 |  | CAPACITY : | 4 | cct
CCT | DESCRIPTION | LOAD (VA) | CB |  | CABLE | TYPE. | COND.
N0. |  | PHASE | P | AT
1 | LIGHTING | 1500 | 1 | 15 | 2x2.5 | THW | 1/2" | 1500 | 6.8182
2 | AIR CONDITION | 1500 | 1 | 20 | 2x4/1.5G | THW | 1/2"
3
4
| VA / PHASE | 3000 | MAIN CB. |  | MAIN CABLE
| TOTAL |  | AT | AF | CABLE | TYPE. | COND.
| DEMAND LOAD /PHASE | 2400 | 30 | 100 | 2x10/4G | THW | 1"
| TOTAL LOAD |  | BRANCH CIRCUIT BREAKER IC 18 KA AT 240 V
| AMP. / PHASE | 10.9091

## DB2
PANEL BOARD LOAD SCHEDULE
PANEL NO. : |  | DB2 |  |  |  | LOCATION : | FLOOR 2
CONNECTED TO : |  | MDB |  |  |  | CAPACITY :
CCT | DESCRIPTION | LOAD (VA) |  |  | CB |  |  | CABLE | TYPE. | COND.
N0. |  | PHASE A | PHASE B | PHASE C | P | AT | AF
1 | LC2A | 7360 |  |  | 2 | 50 | 100 | 2x16/6G | THW | 1" | 3750 | 33.4545
2 | LC2B |  | 4640 |  | 2 | 50 | 100 | 2x16/6G | THW | 1" | 7500
3 | LC2C |  |  | 7360 | 2 | 50 | 100 | 2x16/6G | THW | 1" | 15000
| VA / PHASE | 7360 | 4640 | 7360 | MAIN CB. |  |  | MAIN CABLE
| TOTAL |  | 19360 | VA. | P | AT | AF | CABLE | TYPE. | COND.
| DEMAND LOAD /PHASE | 4416 | 2784 | 4416 | 3 | 50 | 100 | 3x25/16/6G | THW | 1-1/2"
| TOTAL LOAD |  | 11616 | VA. | BRANCH CIRCUIT BREAKER IC 25 KA AT 240 V
| AMP. / PHASE | 20.0727 | 12.6545 | 20.0727
14520

## DB3
PANEL BOARD LOAD SCHEDULE
PANEL NO. : |  | DB3 |  |  |  | LOCATION : | FLOOR 3
CONNECTED TO : |  | MDB |  |  |  | CAPACITY :
CCT | DESCRIPTION | LOAD (VA) |  |  | CB |  |  | CABLE | TYPE. | COND.
N0. |  | PHASE A | PHASE B | PHASE C | P | AT | AF
1 | LC2A | 7360 |  |  | 2 | 50 | 100 | 2x16/6G | THW | 1" | 3750 | 33.4545
2 | LC2B |  | 4640 |  | 2 | 50 | 100 | 2x16/6G | THW | 1" | 7500
3 | LC2C |  |  | 7360 | 2 | 50 | 100 | 2x16/6G | THW | 1" | 15000
| VA / PHASE | 7360 | 4640 | 7360 | MAIN CB. |  |  | MAIN CABLE
| TOTAL |  | 19360 | VA. | P | AT | AF | CABLE | TYPE. | COND.
| DEMAND LOAD /PHASE | 4416 | 2784 | 4416 | 3 | 50 | 100 | 3x25/16/6G | THW | 1-1/2"
| TOTAL LOAD |  | 11616 | VA. | BRANCH CIRCUIT BREAKER IC 25 KA AT 240 V
| AMP. / PHASE | 20.0727 | 12.6545 | 20.0727
14520

## DB4
PANEL BOARD LOAD SCHEDULE
PANEL NO. : |  | DB4 |  |  |  | LOCATION : | FLOOR 4
CONNECTED TO : |  | MDB |  |  |  | CAPACITY :
CCT | DESCRIPTION | LOAD (VA) |  |  | CB |  |  | CABLE | TYPE. | COND.
N0. |  | PHASE A | PHASE B | PHASE C | P | AT | AF
1 | LC2A | 7360 |  |  | 2 | 50 | 100 | 2x16/6G | THW | 1" | 3750 | 33.4545
2 | LC2B |  | 4640 |  | 2 | 50 | 100 | 2x16/6G | THW | 1" | 7500
3 | LC2C |  |  | 7360 | 2 | 50 | 100 | 2x16/6G | THW | 1" | 15000
| VA / PHASE | 7360 | 4640 | 7360 | MAIN CB. |  |  | MAIN CABLE
| TOTAL |  | 19360 | VA. | P | AT | AF | CABLE | TYPE. | COND.
| DEMAND LOAD /PHASE | 4416 | 2784 | 4416 | 3 | 50 | 100 | 3x25/16/6G | THW | 1-1/2"
| TOTAL LOAD |  | 11616 | VA. | BRANCH CIRCUIT BREAKER IC 25 KA AT 240 V
| AMP. / PHASE | 20.0727 | 12.6545 | 20.0727
14520

## DPR
PANEL BOARD LOAD SCHEDULE
PANEL NO. : |  | DPR |  |  |  | LOCATION : | FLOOR 4
CONNECTED TO : |  | MDB |  |  |  | CAPACITY :
CCT | DESCRIPTION | LOAD (VA) |  |  | CB |  |  | CABLE | TYPE. | COND.
N0. |  | PHASE A | PHASE B | PHASE C | P | AT | AF
1 | LIFT | 5000 | 5000 | 5000 | 3 | 40 | 100 | 3x10/6/4G | THW | 1" | 3750 | 22.7273
2 | BOOSTER PUMP | 3500 | 3500 | 3500 | 3 | 30 | 100 | 3x6/4/4G | THW | 1" | 7500
3 | WATER HEATER | 3500 | 3500 | 3500 | 3 | 30 | 100 | 3x6/4/4G | THW | 1"
| VA / PHASE | 12000 | 12000 | 12000 | MAIN CB. |  |  | MAIN CABLE
| TOTAL |  | 36000 | VA. | P | AT | AF | CABLE | TYPE. | COND.
| DEMAND LOAD /PHASE | 10800 | 10800 | 10800 | 3 | 60 | 100 | 3x25/16/6G | THW | 1-1/2"
| TOTAL LOAD |  | 32400 | VA. | BRANCH CIRCUIT BREAKER IC 25 KA AT 240 V
| AMP. / PHASE | 49.0909 | 49.0909 | 49.0909
40500

## LC2A
PANEL BOARD LOAD SCHEDULE
PANEL NO. : |  | LC2A,LC3A,LC4A |  | LOCATION : | FLOOR 2,3,4
CONNECTED TO : |  | DB2,DB3,DB4 |  | CAPACITY : | 8 | cct
CCT | DESCRIPTION | LOAD (VA) | CB |  | CABLE | TYPE. | COND.
N0. |  | PHASE | P | AT
1 | LIGHTING | 1500 | 1 | 15 | 2x2.5 | THW | 1/2" | 1500 | 6.8182
2 | LIGHTING+RECEPTACLE | 1900 | 1 | 15 | 2x2.5/1.5G | THW | 1/2"
3 | LIGHTING+RECEPTACLE | 1200 | 1 | 15 | 2x2.5/1.5G | THW | 1/2"
4 | RECEPTACLE | 1600 | 1 | 15 | 2x2.5/1.5G | THW | 1/2"
5 | AIR CONDITION | 1500 | 1 | 20 | 2x4/1.5G | THW | 1/2"
6 | AIR CONDITION | 1500 | 1 | 20 | 2x4/1.5G | THW | 1/2"
7
8
| VA / PHASE | 9200 | MAIN CB. |  | MAIN CABLE
| TOTAL |  | AT | AF | CABLE | TYPE. | COND.
| DEMAND LOAD /PHASE | 7360 | 50 | 100 | 2x16/6G | THW | 1"
| TOTAL LOAD |  | BRANCH CIRCUIT BREAKER IC 18 KA AT 240 V
| AMP. / PHASE | 33.4545

## LC2B
PANEL BOARD LOAD SCHEDULE
PANEL NO. : |  | LC2B,LC3B,LC4B |  | LOCATION : | FLOOR 2,3,4
CONNECTED TO : |  | DB2,DB3,DB4 |  | CAPACITY : | 6 | cct
CCT | DESCRIPTION | LOAD (VA) | CB |  | CABLE | TYPE. | COND.
N0. |  | PHASE | P | AT
1 | LIGHTING+RECEPTACLE | 1600 | 1 | 15 | 2x2.5 | THW | 1/2" | 1600 | 7.2727
2 | LIGHTING+RECEPTACLE | 1300 | 1 | 15 | 2x2.5/1.5G | THW | 1/2"
3 | RECEPTACLE | 1400 | 1 | 15 | 2x2.5/1.5G | THW | 1/2"
4 | AIR CONDITION | 1500 | 1 | 20 | 2x4/1.5G | THW | 1/2"
5
6
| VA / PHASE | 5800 | MAIN CB. |  | MAIN CABLE
| TOTAL |  | AT | AF | CABLE | TYPE. | COND.
| DEMAND LOAD /PHASE | 4640 | 50 | 100 | 2x16/6G | THW | 1"
| TOTAL LOAD |  | BRANCH CIRCUIT BREAKER IC 18 KA AT 240 V
| AMP. / PHASE | 21.0909

## LC2C
PANEL BOARD LOAD SCHEDULE
PANEL NO. : |  | LC2C,LC3C,LC4C |  | LOCATION : | FLOOR 2,3,4
CONNECTED TO : |  | DB2,DB3,DB4 |  | CAPACITY : | 18 | cct
CCT | DESCRIPTION | LOAD (VA) | CB |  | CABLE | TYPE. | COND.
N0. |  | PHASE | P | AT
1 | LIGHTING | 1500 | 1 | 15 | 2x2.5 | THW | 1/2" | 1500 | 6.8182
2 | LIGHTING+RECEPTACLE | 1900 | 1 | 15 | 2x2.5/1.5G | THW | 1/2"
3 | LIGHTING+RECEPTACLE | 1200 | 1 | 15 | 2x2.5/1.5G | THW | 1/2"
4 | RECEPTACLE | 1600 | 1 | 15 | 2x2.5/1.5G | THW | 1/2"
5 | AIR CONDITION | 1500 | 1 | 20 | 2x4/1.5G | THW | 1/2"
6 | AIR CONDITION | 1500 | 1 | 20 | 2x4/1.5G | THW | 1/2"
7
8
| VA / PHASE | 9200 | MAIN CB. |  | MAIN CABLE
| TOTAL |  | AT | AF | CABLE | TYPE. | COND.
| DEMAND LOAD /PHASE | 7360 | 50 | 100 | 2x16/6G | THW | 1"
| TOTAL LOAD |  | BRANCH CIRCUIT BREAKER IC 18 KA AT 240 V
| AMP. / PHASE | 33.4545

## tr
|  |  | FREE AIR |  |  | THW ท่อโลหะลอย
TR | AMP Max | CB | 1 | 2 | 3 | 1 | 2 | 3 | G
30 | 43.3025 | 40 | 4x16 |  |  | 4x16 | 8x | 12x | 10
50 | 72.1709 | 70 | 4x35 |  |  | 4x35 | 8x | 12x | 10
100 | 144.3418 | 125 | 4x70 | 8x35 |  | 4x | 8x | 12x | 25 | 2x10
160 | 230.9469 | 225 | 4x120 | 8x50 |  | 4x | 8x | 12x | 35 | 2x10
200 | 288.6836 | 250 | 4x150 | 8x70 |  | 4x | 8x | 12x | 35 | 2x25
250 | 360.8545 | 350 | 4x185 | 8x95 | 12x50 | 4x | 8x | 12x | 35 | 2x35
315 | 454.6767 | 450 | 4x240 | 8x120 | 12x70 | 4x | 8x | 12x | 50 | 2x35
400 | 577.3672 | 500 | 4x400 | 8x150 | 12x95 | 4x | 8x | 12x | 70 | 2x35
500 | 721.709 | 700 | 4x500 | 8x185 | 12x120 | 4x | 8x | 12x | 95 | 2x35
630 | 909.3533 | 900 |  | 8x240 | 12x150 | 4x | 8x | 12x |  | 2x50
800 | 1154.7344 | 1100 |  | 8x400 | 12x240 | 4x | 8x | 12x |  | 2x70
1000 | 1443.418 | 1400 |  | 8x500 | 12x300 | 4x | 8x | 12x |  | 2x95